ENGINEERING SPECIFICATION

EMERGENCY VOICE EVACUATION/MASS NOTIFICATION CONTROL PANEL

PART 1.0	GENERAL

1.1	DESCRIPTION:

A. 	This section of the specification includes the furnishing, installation, connection and testing of the microprocessor controlled Voice Evacuation/Mass Notification control panel.

B. 	The Voice Evacuation/Mass Notification panel shall comply with NFPA 72 requirements.

1.	The Secondary Power Source of the Voice Evacuation/Mass Notification panel will be capable of providing at least 24 hours of backup power with the ability to sustain 15 minutes in alarm at the end of the backup period.

C. 	The Voice Evacuation/Mass Notification panel shall be manufactured by an ISO 9001 certified company and meet the requirements of BS EN9001: ANSI/ASQC Q9001-1994.

D. 	The Voice Evacuation/Mass Notification panel and peripheral devices shall be manufactured 100% by a single U.S. manufacturer (or division thereof).

E. 	Underwriters Laboratories Inc. (UL) - USA:

1.	UL 864 Standard for Control Units for Fire Protective Signaling Systems

2.	UL 1711 Amplifiers for Fire Protective Signaling Systems

3.	UL 2572 Communication and Control Units for Mass Notification Systems

4.	NEC Article 250 Grounding

5.	NEC Article 300 Wiring Methods

6.	NEC Article 760 Fire Protective Signaling Systems

7.	Compliant with Unified Facilities Criteria UFC 4-021-01

F.	The Voice Evacuation/Mass Notification panel shall be ANSI 864, 9th Edition Listed.  Systems listed to ANSI 864, 8th edition (or previous revisions) shall not be accepted.

G. 	The installing company shall employ NICET (minimum Level II Fire Alarm Technology) technicians on site to guide the final check-out and to ensure the systems integrity.

1.2 	SCOPE:

A. 	A microprocessor-controlled Voice Evacuation/Mass Notification control panel shall be installed in accordance with the project specifications and drawings.

1.3	SUBMITTALS

A.	General:

1. 	Two copies of all submittals shall be submitted to the Architect/Engineer for review.

2.	All references to manufacturer's model numbers and other pertinent information herein is intended to establish minimum standards of performance, function and quality. Equivalent compatible UL-listed equipment from other manufacturers may be substituted for the specified equipment as long as the minimum standards are met.

3.	For equipment other than that specified, the contractor shall supply proof that such substitute equipment equals or exceeds the features, functions, performance, and quality of the specified equipment.

B. 	Shop Drawings:

1.	Sufficient information, clearly presented, shall be included to determine compliance with drawings and specifications.

2.	Include manufacturer's name(s), model numbers, ratings, power requirements, equipment layout, device arrangement, complete wiring point-to-point diagrams, and conduit layouts.

3.	Show system layout, configurations, and terminations.

C. 	Manuals:

1.	Submit simultaneously with the shop drawings, complete operating and maintenance manuals listing the manufacturer's name(s), including technical data sheets.

2.	Wiring diagrams shall indicate internal wiring for each device and the interconnections between the items of equipment.

3.	Provide a clear and concise description of operation that gives, in detail, the information required to properly operate the equipment and system.

D. 	Software Modifications

1.	Provide the services of a qualified technician to perform all system software modifications, upgrades or changes.  Response time of the technician to the site shall not exceed 4 hours.

2.	Provide all hardware, software, programming tools and documentation necessary to modify the Voice Evacuation/Mass Notification Control Panel on site. Modification includes addition and deletion of messages, circuits, zones and changes to system operation. The system structure and software shall place no limit on the type or extent of software modifications on-site.

1.4 	GUARANTY:

A.	All work performed and all material and equipment furnished under this contract shall be free from defects and shall remain so for a period of at least one (1) year from the date of acceptance. The full cost of maintenance, labor and materials required to correct any defect during this one year period shall be included in the submittal bid.

1.5	MAINTENANCE:

A. 	Maintenance and testing shall be on a semi-annual schedule or as required by the local AHJ. A preventive maintenance schedule shall be provided by the contractor describing the protocol for preventive maintenance. The Voice Evacuation/Mass Notification Control Panel shall be tested in accordance with the requirements of NFPA 72.

B. 	As part of the bid/proposal, include a quote for a maintenance contract to provide all maintenance, tests, and repairs described below. Include also a quote for unscheduled maintenance/repairs, including hourly rates for technicians trained on this equipment, and response travel costs for each year of the maintenance period. Submittals that do not identify all post contract maintenance costs will not be accepted. Rates and costs shall be valid for the period of five (5) years after expiration of the guaranty.

1.6	POST CONTRACT EXPANSIONS:

A. 	The contractor shall have the ability to provide parts and labor to expand the system specified, if so requested, for a period of five (5) years from the date of acceptance.

B. 	As part of the submittal, include a quotation for all parts and material, and all installation and test labor as needed to increase the number of speaker zones or wattage by ten percent (10%).

C. 	The quotation shall include installation, test labor, and labor to reprogram the system for this 10% expansion. If additional Voice Evacuation/Mass Notification Control Panel hardware is required, include the material and labor necessary to install this hardware.

D. 	Do not include cost of conduit or wire or the cost to install conduit or wire except for labor to make final connections at the Voice Evacuation/Mass Notification Control Panel.

E. 	Submittals that do not include this estimate of post contract expansion cost will not be accepted.

1.7 	APPLICABLE STANDARDS AND SPECIFICATIONS:

A.	The specifications and standards listed below form a part of this specification. The system shall fully comply with the latest issue of these standards, if applicable.

B. 	National Fire Protection Association (NFPA) - USA:

1.   	No. 70	National Electric Code (NEC)

2.  	No. 72	National Fire Alarm Code

3.   	No. 101 	Life Safety Code

C. 	The system and its components shall be Underwriters Laboratories, Inc. listed under the appropriate UL testing standard as listed herein for fire alarm applications and the installation shall be in compliance with the UL listing.

D. 	Local and State Building Codes.

E. 	All requirements of the Authority Having Jurisdiction (AHJ).

1.8 	APPROVALS:

A. 	The system shall have proper listing and/or approval from the following nationally recognized agencies:

1.	UL	  Underwriters Laboratories Inc (Ninth Edition)

2.      CSFM	  California State Fire Marshal

3.      NYFD	  New York Fire (City) Department Approved (NYFD COA)

PART 2.0 	PRODUCTS

2.1 	EQUIPMENT AND MATERIAL, GENERAL:

A. 	All equipment and components shall be new, and the manufacturer's current model. The materials, appliances, equipment and devices shall be tested and listed by a nationally recognized approvals agency for use as part of a fire protective signaling system, meeting the National Fire Alarm Code.

B. 	All equipment and components shall be installed in strict compliance with manufacturers' recommendations. Consult the manufacturer's installation manuals for all wiring diagrams, schematics, physical equipment sizes, etc., before beginning system installation.

C. 	All equipment shall be attached to walls and ceiling/floor assemblies and shall be held firmly in place (e.g., speakers shall not be supported solely by suspended ceilings). Fasteners and supports shall be adequate to support the required load.

2.2 	CONDUIT AND WIRE:

A. 	Conduit:

1.	Conduit shall be in accordance with The National Electrical Code (NEC), local and state requirements.

2. 	Where required, all wiring shall be installed in conduit or raceway.  Conduit fill shall not exceed 40 percent of interior cross sectional area where three or more cables are contained within a single conduit.

3. 	Cable must be separated from any open conductors of power, or Class 1 circuits, and shall not be placed in any conduit, junction box or raceway containing these conductors, per NEC Article 760.

4.	All circuits shall be provided with transient suppression devices and the system shall be designed to permit simultaneous operation of all circuits without interference or loss of signals.

5.	Conduit shall not enter the Voice Evacuation/Mass Notification Control Panel, or any other remotely mounted panel equipment or backboxes, except where conduit entry is specified by the Voice Evacuation/Mass Notification Control Panel manufacturer.

6.	Conduit shall be 3/4 inch (19.1 mm) minimum.

B. 	Wire:

1.	All Voice Evacuation/Mass Notification Control Panel wiring shall be new.

2.	Wiring shall be in accordance with local, state and national codes (e.g., NEC Article 760) and as recommended by the manufacturer of the Voice Evacuation/Mass Notification Control Panel. Number and size of conductors shall be as recommended by the Voice Evacuation/Mass Notification Control Panel, but not less 14 AWG (1.63 mm) for Notification Appliance Circuits.

3.	All wire and cable shall be listed and/or approved by a recognized testing agency for use with a protective signaling system.

4.	Wire and cable not installed in conduit shall have a fire resistance rating suitable for the installation as indicated in NEC 760 (e.g., FPLR).

5. 	All field wiring shall be electrically supervised for open circuit and ground fault.

C. 	Terminal Boxes, Junction Boxes and Cabinets:

1.	All boxes and cabinets shall be UL listed for their use and purpose.

D. 	The Voice Evacuation/Mass Notification Control Panel shall be connected to a separate dedicated branch circuit, maximum 20 amperes. This circuit shall be labeled at the main power distribution panel as Voice Evacuation/Mass Notification Control Panel. Voice Evacuation/Mass Notification Control Panel primary power wiring shall be 12 AWG. The panel cabinet shall be grounded securely to either a cold water pipe or grounding rod.

1. 	The Voice Evacuation/Mass Notification Control Panel notification circuit (NACs 1) shall also automatically synchronize any of the following manufacturer’s notification appliances connected to them: System Sensor, Wheelock, or Gentex with no need for additional synchronization modules.

2.3	Voice Evacuation/Mass Notification Control Panel:

A. 	The Voice Evacuation/Mass Notification Control Panel shall be a NOTIFIER FirstCommand NFC-50/100 and shall contain a microprocessor-based Central Processing Unit (CPU). The CPU shall distribute and control emergency voice messages over the speaker circuits.

B. 	The system shall provide the capability to interface to LOC (Local Operator Console), Distributed Audio Amplifiers, Remote Page Unit, Remote Microphone, Fire Fighter Telephone Unit and Remote Telephone Zone Module from the same manufacturer.

C. 	Shall have as minimum requirements:

1.	Integral 50 Watt, 25 Vrms audio amplifier with optional converter for 70.7 volt systems. The system shall be capable of expansion to 100 watts total via the insertion of an additional 50-watt audio amplifier module (can be used as a backup amplifier) into the same cabinet. With the addition of optional circuit expander modules and remote Distributed Amplifiers the system can be expanded up to 24 speaker circuits and 1100 watts.

2. 	Speaker circuit that can be wired both Class A and B.

3. 	Integral Digital Message Generator with a memory capacity for up to 60 seconds per messaging.  The Digital Message Generator shall be capable of producing fourteen distinct messages (60 seconds each). Field-selectable message and custom message recording capability using the local microphone, a USB port, or an external audio input.

4. 	Built in alert tone patterns with ANSI, March Code, California, Steady, Alert Tone, Hi-Lo, ANSI Whoop, Continuous Whoop, or No Tone is field programmable. Tone Prior to transmitting a message, the Voice Evacuation/Mass Notification Control Panel can be programmed to produce a pre-announce and post-announce tone.

a.	Leading Tone Duration If a pre-announce tone is desired; select the length of time it will play before a message is broadcasted. Select 4, 8, 12, 16, 20, 24, or 28 seconds. In a pre-announce tone is not desired, select 0 seconds.

b.	Trailing Tone Duration Select the length of time for the post-message announcement tone. Select 4, 8, 12, 16, 20, 24, 28, or 32 seconds from the drop-down menu.

c.	Repeat Cycle Select the number of times the message will be repeated during an alarm. A message can be repeated 0, 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, or an Infinite amount of times.

5. 	The Voice Evacuation/Mass Notification Control Panel will be capable of detecting and annunciating the following conditions: Loss of Power (AC and DC), System Trouble, Ground Fault, Alarm, Microphone Trouble, Message Generator Trouble, Tone Generator Trouble, and Amplifier Fault.

6. 	The Voice Evacuation/Mass Notification Control Panel shall be fully supervised including microphone, amplifier output, message generator, speaker wiring, and tone generation.

7. 	Speaker outputs shall be fully power-limited.

8. 	Amplifiers will be supplied power independently to eliminate a short on one circuit from affecting other circuits.

9. 	The Voice Evacuation/Mass Notification Control Panel will provide full supervision on both active (alarm or music) and standby conditions.

10. 	With the addition of an optional internal amplifier and a circuit expander module the main NFC-50/100 can be configured for up to 100 watts and 8 speaker circuits.

11. 	Optional distributed amplifiers shall be available to expand the system with up 24 speaker circuits up to 1100 watts.

12. 	Wiring terminals shall be removable terminal blocks (Wire Gauge 12 – 18 AWG) for ease of servicing.

13. 	Voice Evacuation/Mass Notification Control Panel will provide 2 amp Notification Appliance Circuit (NAC) output with sync generator or follower for System Sensor, Wheelock or Gentex protocols. The NAC shall be capable of One (1) Style Y (Class B) or Style Z (Class A) circuit.

14. 	Shall have eight Command Input Circuits to activate messages via reverse polarity or contact closures.

15. 	Built in External Audio Input can be used for background music.

16. 	On-board battery charger which supports charging up to 26 AH batteries     (cabinet holds up to 18AH batteries).

17. 	Programmable delay of immediate, 2 hours or 6 hours reporting of AC Loss.

18. 	Built in Piezo sounder for local trouble.

19. 	Stores the events in the 100 Event History log.

20. 	Shall have Console Lamp Test switch and shall activate all system LEDs including Remote Consoles.

21. 	Shall have three Form-C relays:

a.	AC Power Loss Relay

b. 	System Trouble Relay

c.	MNS Active (For Mass Notification signage)

22. 	Shall have a Special Application (auxiliary power) output for addressable modules when interfaced with compatible addressable FACPs and End-of-Line power supervision relays.

23. 	Shall be capable of Speaker Volume Control. The Supervised Volume Control will allow manual volume setting for telephone paging and background music for a specific speaker or speaker zone.

24. 	Shall have a Night Ring input allows a building’s Private Branch Exchange (PBX) to activate the Voice Evacuation/Mass Notification panel.

25. 	The Voice Evacuation/Mass Notification panel can communicate in any combination up to eight (8) external remote consoles:

a.	Optional Remote Microphone

b.	Optional Remote Page Unit

c.	Optional Local Operator Console

26. 	The Voice Evacuation/Mass Notification panel can communicate in any combination up to eight (8) external distributed audio amplifiers:

a.	Optional Distributed Amplifier, 50 watts.

b.	Optional Distributed Amplifier, 125 watts.

27. 	Shall be capable of integrating with firefighter telephone system that provides secure and reliable communications. The firefighter telephone system will allow for up to ten users to plug in to a remote telephone jack and communicate simultaneously within a building.

28. 	Shall be capable of secure access to the Voice Evacuation/Mass Notification panel via cell phone or other remote telephone.

29. 	The Voice Evacuation/Mass Notification panel can be integrated by an FACP via the ANN/ACS (EIA-485) link. Compatible FACPs include the NFS-320, NFS2-640 and the NFW2-100 (FireWarden-100-2).

30. 	The Voice Evacuation/Mass Notification panel integrates with the NFS-320, NFS2-640 and the NFW2-100 (FireWarden-100-2) will report Mass Notification events to the Central Station.

31. 	The Voice Evacuation/Mass Notification panel can be interfaced with other UL Listed Fire Alarm Control Panels via activation of reverse polarity or by contact closure.

D. 	Speakers:

1.	All speakers shall operate on 25 or 70 VRMS with field selectable output taps from 0.25 to 2.0 Watts.

2.	Speakers in corridors and public spaces shall produce a minimum sound levels of 75 dBA output at 10 feet (3m).

3.	The plug-in speaker allows the installer to pre-wire mounting plates and dress the wires before plugging in the speakers.

4.	Flush mount applications are achievable without the need for an extension ring.

5.	Frequency response shall be a minimum of 400 HZ to 4000 HZ.

6.	Rotary switch simplifies field selection of speaker voltage and power settings.

E. 	Enclosures:

1.	The Voice Evacuation/Mass Notification panel shall be housed in a UL-listed cabinet suitable for surface mounting. The cabinet and front shall be corrosion protected and painted red via the powder coat method with manufacturer's standard finish.

2.	The back box and door shall be constructed of steel with provisions for electrical conduit connections into the sides and top.

3.	The door shall provide a key lock and shall provide for the viewing of all indicators.

F. 	Power Supply:

1.	The main power supply for the Voice Evacuation/Mass Notification panel shall provide up to 7.5 amps of available power for the panel and peripheral devices.

2.	Provisions will be made to allow the audio-visual power to be increased as required by adding modular expansion audio-visual power supplies.

3.	The power supply shall provide an integral battery charger or may be used with an external battery and charger systems. Battery arrangement may be configured in the field.

4.	The main power supply shall continuously monitor all field wires for earth ground conditions.

5.	The main power supply shall operate on 120 VAC, 60 Hz or 240 VAC, 50 Hz, and shall provide all necessary power for the Voice Evacuation/Mass Notification panel.

G. 	BATTERIES:

1.	Upon loss of Primary (AC) power to the Voice Evacuation/Mass Notification panel, the batteries shall have sufficient capacity to power the Voice Evacuation/Mass Notification panel for required standby time (24 or 60 hours) followed by 15 minutes of alarm.

2.	The batteries are to be completely maintenance free. No liquids are required. Fluid level checks for refilling, spills, and leakage shall not be required.

PART 3.0	EXECUTION

3.1 	INSTALLATION:

A.	Installation shall be in accordance with the NEC, NFPA 72, local and state codes, as shown on the drawings, and as recommended by the major equipment manufacturer.

B. 	All conduit, junction boxes, conduit supports and hangers shall be concealed in finished areas and may be exposed in unfinished areas. Smoke detectors shall not be installed prior to the system programming and test period. If construction is ongoing during this period, measures shall be taken to protect speakers from contamination and physical damage.

3.2	TEST:

A.	The service of a competent, factory-trained engineer or technician authorized by the manufacturer of the fire alarm equipment shall be provided to technically supervise and participate during all of the adjustments and tests for the system. All testing shall be in accordance with NFPA 72.

B. 	Before energizing the cables and wires, check for correct connections and test for short circuits, ground faults, continuity, and insulation.

C. 	Open and short notification appliance circuits and verify that trouble signal actuates.

D. 	Ground all circuits and verify response of trouble signals.

E. 	Check presence and audibility of tone at all alarm notification devices.

F. 	When the system is equipped with optional features, the manufacturer's manual shall be consulted to determine the proper testing procedures. This is intended to address such items as verifying voice messages.

3.3	FINAL INSPECTION:

A. 	At the final inspection a minimum NICET Level II technician shall demonstrate that the system functions properly in every respect.

3.4	INSTRUCTION:

A. 	Instruction shall be provided as required for operating the system. Hands-on demonstrations of the operation of all system components and the entire system including program changes and functions shall be provided.

B. 	The contractor or installing dealer shall provide a user manual indicating "Sequence of Operation."

END OF SECTION